## Slide 1: COMBINED HEAT AND POWER (CHP) SYSTEM OPTIMIZATION USING ENERGY, EXERGY AND THERMODYNAMIC ANALYSIS-Alumina Refinery Power Plant Optimization – Two Case Studies (A21) Quamie N. Mortley1, Winston A. Mellowes2
Author1 Chemical and Energy Engineering Consultant
Author2 Professor Emeritus

## Slide 2
INTRODUCTION
The science of thermodynamics is built primarily on two fundamental natural laws, known as the first and the second laws. The first law of thermodynamics is simply an expression of the conservation of energy principle. It asserts that energy is a thermodynamic property, and that during an interaction, energy can change from one form to another but the total amount of energy remains constant. The second law of thermodynamics asserts that energy has quality as well as quantity, and actual processes occur in the direction of decreasing quality of energy. The high-temperature thermal energy is degraded as it is transferred to a lower temperature body. The attempts to quantify the quality or “work potential” of energy in the light of the second law of thermodynamics has resulted in the definition of the properties entropy and exergy.
Exergy is defined as: The maximum useful work which can be extracted from a system as it reversibly comes into equilibrium with its environment.

## Slide 3: OBJECTIVES
Powerhouse Optimization - Low Grade Heat Minimization/Recovery
A large amount of low-grade heat in the temperature range 30 oC and 180 oC are readily available in process industries, and a wide range of technologies can be employed to recover and utilize low-grade heat.
The basis of this optimization is to minimize losses to the low temperature sink. The infinite low temperature sink is the surroundings.
The route to exergy losses to the surroundings is via the condensing steam turbines. The steam exhaust from these turbines are sent to the condensers which are cooled by cooling water from the cooling tower which dissipates heat to the atmosphere.

## Slide 4: METHODOLOGY
The basis for the reconfiguration (optimization) is to remove the condensing steam turbines from service, thereby reducing losses to the low temperature sink.
Case Study 1 - 1,650,000 t/y Alumina Refinery. Remove 20 MW of condensing steam turbine power and 2 steam boilers (545 t/h) from service. Add 35 MW of auxiliary power.
Case Study 2 -650,000 t/y Alumina Refinery. Remove 6.9 MW of condensing steam turbine and 1 steam boiler (70 t/h) from service. Add 3.5 MW of grid power.

## Slide 5: RESULTS
Case Study 1
Table 1 Process Variables and Fuel Use
Production (t/d) | 4,550 | 4,550
Boilers On-line | 4 | 2
Total Steam (t/h) | 995 | 635
Powerhouse Steam (t/h) | 385 | 25
Process Steam (t/h) | 610 | 610
Total Power (MW) | 50 | 50
Condensing Power (MW) | 18 | 0
Supplementary Power (MW) | 0 | 35
BFO Consumption (t/d) | 1365 | 840

## Slide 6: RESULTS
Case Study 2
Table 2 Process Variables and Fuel Use
Production (t/d) | 1,800 | 1,800
Boilers On-line | 4 | 3
Total Steam (t/h) | 274 | 238
Powerhouse Steam (t/h) | 73 | 34
Process Steam (t/h) | 201 | 204
Total Power (MW) | 20.5 | 20.5
Condensing Power (MW) | 6.9 | 0
Auxiliary Power (MW) | 0.4 | 3.5
BFO Consumption (t/d) | 486 | 422

## Slide 7: RESULTS
Savings after powerhouse reconfiguration:
Case Study 1 – Gross fuel savings US$78,470,000.
Case Study 2 - Gross fuel savings US$9,565,000.

## Slide 8: REFERENCES
Rant Z. Exergy, a New Word for Technical Available Work”, Forschung auf dem Gebiete des Ingenieurwesens, 22, (1956).
Van Gool, W., Bruggink, J.C., (Editors) (1985). Energy and Time in the Economic and Physical Sciences, North-Holland Publishing Company.
Cengel, Y.A., Michael, A.B., Thermodynamics: An Engineering Approach, 6th Edition, McGraw Hill Companies, Inc., New York.
Kotas, T.J., (1985). The Exergy Method of Thermal Plant Analysis, Butterworths Publishing Company, London.

## Slide 9
THANK YOU!